## 0. System Data
General Inputs |  | General Inputs will fill in yellow-box values in subsequent tabs
Desired MFO (kW) | 3000 | customer to provide
Power Factor Req. | 1 | What guidance do we give the team here? Look for small/large generator agreement?
Itxn Voltage (kV) | 25 | customer to provide

## 1. MFO Sizing
Inputs
Desired MFO (kW) | 3000 |  | Losses from Subsequent Tabs
Power Factor Req. | 1 | use "1" if no PF requirement | Tie Line | Collector* | GSU | ISU** | Totals
Losses (kW) | 108.3309 | Enter "0" for lossless system, or use table to right | 93.4053 | 0 | 0 | 14.9256 | 108.3309 | kW
Losses (kVAR) | 165.9636 | Enter "0" for lossless system, or use table to right | 16.708 | 0 | 0 | 149.2556 | 165.9636 | kVAR
Inverter | SHP 150 | choose inverter that results in smallest qty and highest loading | *Collector may need additional hand calcs depending on number of loops and parallel config
**ISU losses need to be multiplied by number of inverters
Intermediate Calcs |  |  | ^used the rough 1150' length between poi and xfmr |  |  | ^isu losses are just considered as the single 3MW xfmr losses
Total Power Needed (kW) | 3165.9636
Inv. Real Power @ PF (kW) | 4324
Inv. App. Power (kVA) | 4600
Fractional Inv. Qty Needed | 0.73218
Inv. Loading @ Full Qty | 3.661%
Outputs
Total Qty Needed | 20 | originally calculated 22
Ttl Inv Capacity (kW) | 86480
Inverter Derating Each (kW) | 4165.7018 | Does kW derating also derate kVA?
Ttl Inv kVA | 92000
Good example (Roan Solar):
https://drive.google.com/file/d/1UT0GN63BvajsMvh_xJxIl1zv_68apIt-/view?pli=1

## 2. Tie Line
Inputs
T-Line MVA (=MFO) | 3
Itxn Voltage (kV) | 25
Power Factor Req. | 1
Line Length (kft) | 7.92
Intermediate Calcs
High Side Current (A) | 69.282
ACSR Code | Turkey
Conductor KCMIL | #6
Conductor Ampacity | 105
Resistance (ohms/kft) | 0.819
Cap. Reactance (Mohms*kft) | 0.7512
Ind. Reactance (ohms/kft) | 0.1465
Output
Total R resistance (ohms) | 6.4865
Total X reactance (ohms) | 1.1603
Total B susceptance (siemens) | 1.0543e-05
pu Output
S-B base MVA | 100
Z-B base impedance (ohms) | 6.25
Y-B base admittance (siemens) | 0.16
Total R (pu) | 1.0378
Total X (pu) | 0.18564
Total B (pu) | 6.5895e-05
Losses
Real Losses (kW) | 93.4053
Reactive Losses (kVAR) | 16.708
Need R1, R0, X1, X0, B1, B0 for some utils (like Prairie Power); but do not have pos. sequence and zero sequence in ACSR spec sheet - not sure how to do

## 3a. GSU 3-Winding
Inputs
MFO | 3
Interconnection Voltage (kV) | 25
Power Factor Requirement | 1
MVA | 20 | Select whole number >= MFO
MVA Base, S-B | 20 | typically equal to ONAN rating
Intermediate Calcs
X/R | 19
%Z | 8%
%Z H-T (three winding) | 12% | Per PJM 150% of Z1
%Z L-T (three winding) | 2.667% | Per PJM 33% of Z1
ONAN Rating (MVA) | 20
ONAF1 Rating (MVA) | 27 | Using "1.33" factor for now
ONAF2 Rating (MVA) | 36 | Using "1.33" factor for now
need intermediate voltage as well - not sure how to calculate
Outputs
R1,R0 Hi-Lo (ohms) | 0.0042047 | positive and zero sequence are the same for transformers
X1,X0 Hi-Lo (ohms) | 0.079889
R1,R0 Hi-Tertiary (ohms) | 0.0063071
X1,X0 Hi-Tertiary (ohms) | 0.11983
R1,R0 Lo-Tertiary (ohms) | 0.0014016
X1,X0 Lo-Tertiary (ohms) | 0.02663
Z-base Z-B (ohms) | 31.25
Z impedance (ohms) | 2.5
R resistance (ohms) | 0.1314
X reactance (ohms) | 2.4965
Losses
Required Apparent Power (kVA) | 20000
High Side Current (A) | 461.8802
Real Losses (kW) | 84.0941
Reactive Losses (kVAR) | 1597.7885

## 3b. GSUISU 2-Winding
Inputs
MFO | 2.5 | May not be needed for ISU calcs
Interconnection Voltage (kV) | 25 | May not be needed for ISU calcs
Power Factor Requirement | 1 | May not be needed for ISU calcs
ISU High Voltage (kV) | 12.47
MVA | 2.5 | Select whole number >= inverter kVA (or MFO for GSU)
MVA Base S-B | 2.5
Intermediate Calcs
X/R | 10
%Z | 6%
ONAN Rating (MVA) | 2.5
ONAF1 Rating (MVA) | 4 | Using "1.33" factor for now
ONAF2 Rating (MVA) | 6 | Using "1.33" factor for now
Outputs
R1,R0 (ohms) | 0.0059702 | positive and zero sequence are the same for transformers
X1,X0 (ohms) | 0.059702
Z-base Z-B (ohms) | 62.2004
Z impedance (ohms) | 3.732
R resistance (ohms) | 0.37135
X reactance (ohms) | 3.7135
Losses
Required Apparent Power (kVA) | 2500
High Side Current (A) | 115.7478
Real Losses (kW) | 14.9256
Reactive Losses (kVAR) | 149.2556

## 4. Collector System
Inputs
Power Factore Requirement | 1
Inverters in Loop | 1
Loop Voltage (kV) | 12.47
Inverter | SHP 150
Loop Length (kft) | 1 | *assuming inverters are evenly spaced
Intermediate Calcs
Inverter Power | 4324
Inverter Current | 200.1975
Loop Current | 200.1975
Conductor KCMIL | 4/0 | *assuming same conductor size for whole loop
Conductor Ampacity | 230
Resistance (ohms/kft) | 0.105 |  |  |  |  | This sheet is incomplete for multiple loops, if present, which would need to be summed for overall equivalence
Cap. Reactance (Mohms*kft) | 0.056
Ind. Reactance (ohms/kft) | 0.05
R1 (ohms/kft) | 0.106
X1 (ohms/kft) | 0.049
R0 (ohms/kft) | 0.43
X0 (ohms/kft) | 0.245
Output
R resistance (ohms) | 0.105
X-C cap. reactance (Mohms) | 0.056
X-L ind. reactance (ohms) | 0.05
R1 (ohms) | 0.106
X1 (ohms) | 0.049
R0 (ohms) | 0.43
X0 (ohms) | 0.245
X total reactance (ohms) | 0.05 | *I think this is just X-L; do not consider X-C?
B susceptance (siemens) |  | *In old intxn spreadsheet "Collector System Calcs" this equation is X-C/(R1^2+X-C) - not sure where this comes from; elsewhere this is just 1/X-C
Need B1, B0 for some utils (like Prairie Power) - not sure how to calculate
pu Output
S-B base MVA | 100
Z-B base impedance (ohms) | 1.555
Y-B base admittance (siemens) | 0.64308
Losses |  |  | Segment | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Total Real Losses (kW) | 12.6249 |  | Current | 200.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Reactive Losses (kVAR) | 6.0119 |  | kW Losses | 12.6249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | kVAR Losses | 6.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ACSR Cable Data
Code | Size (KCMIL) | Ampacity | Resistance (ohms/kft) | Cap. Reactance (Mohms*kft) | Ind. Reactance (ohms/kft)
Mallard | 795 | 920 | 0.0259 | 0.4773 | 0.0746
Drake | 795 | 910 | 0.0262 | 0.4818 | 0.0756 | https://prysmian-group.dcatalog.com/v/Electric-Utility-(US)/?page=106
Cuckoo | 795 | 905 | 0.0263 | 0.484 | 0.0762
Puffin | 795 | 900 | 0.0265 | 0.4862 | 0.0767
Turbit | 795 | 890 | 0.0266 | 0.4882 | 0.0772
Condor | 795 | 880 | 0.0276 | 0.4841 | 0.076
Macaw | 795 | 870 | 0.0279 | 0.4895 | 0.0774
Tern | 795 | 870 | 0.0278 | 0.4882 | 0.077
Coot | 795 | 865 | 0.028 | 0.4916 | 0.0779
Redwing | 715.5 | 860 | 0.0288 | 0.4857 | 0.0758
Starling | 715.5 | 850 | 0.029 | 0.4901 | 0.0768
Stilt | 715.5 | 845 | 0.0292 | 0.4923 | 0.0774
Gannet | 666.6 | 815 | 0.0312 | 0.4956 | 0.0777
Flamingo | 666.6 | 810 | 0.0313 | 0.4978 | 0.0782
Scoter | 636 | 800 | 0.0323 | 0.4948 | 0.0772
Egret | 636 | 800 | 0.0323 | 0.4948 | 0.0772
Grosbeak | 636 | 790 | 0.0326 | 0.4993 | 0.0782
Rook | 636 | 785 | 0.0328 | 0.5015 | 0.0787
Goldfinch | 636 | 780 | 0.033 | 0.5037 | 0.0793
Wood Duck | 605 | 775 | 0.0339 | 0.4988 | 0.0778
Teal | 605 | 775 | 0.034 | 0.4988 | 0.0778
Kingbird | 636 | 775 | 0.0331 | 0.5075 | 0.0804
Turacos | 636 | 775 | 0.0331 | 0.5057 | 0.0798
Squab | 605 | 765 | 0.0343 | 0.5033 | 0.0788
Peacock | 605 | 760 | 0.0344 | 0.5054 | 0.0793
Swift | 636 | 750 | 0.0349 | 0.5091 | 0.0805
Eagle | 556.5 | 735 | 0.0369 | 0.5053 | 0.0787
Parakeet | 556.5 | 725 | 0.0374 | 0.5119 | 0.0803
Dove | 556.5 | 725 | 0.0372 | 0.5098 | 0.0798
Sapsucker | 556.5 | 720 | 0.0376 | 0.5142 | 0.0808
Tody | 556.5 | 715 | 0.0378 | 0.5162 | 0.0814
Osprey | 556.5 | 710 | 0.0378 | 0.518 | 0.0819
Heron | 500 | 690 | 0.041 | 0.5137 | 0.08
Hen | 477 | 670 | 0.043 | 0.5174 | 0.0805
Hawk | 477 | 660 | 0.0434 | 0.5219 | 0.0815
Flicker | 477 | 655 | 0.0436 | 0.524 | 0.0821
Tailorbird | 477 | 650 | 0.044 | 0.5282 | 0.0831
Toucan | 477 | 650 | 0.0438 | 0.5262 | 0.0826
Pelican | 477 | 645 | 0.044 | 0.53 | 0.0837
Lark | 397.5 | 595 | 0.0515 | 0.5317 | 0.0826
Ibis | 397.5 | 590 | 0.0521 | 0.5362 | 0.0836
Brant | 397.5 | 585 | 0.0523 | 0.5383 | 0.0841
Ptarmigan | 397.5 | 580 | 0.0527 | 0.5424 | 0.0852
Stork | 397.5 | 580 | 0.0525 | 0.5404 | 0.0847
Chickadee | 397.5 | 575 | 0.0528 | 0.5443 | 0.0857
Oriole | 336.4 | 535 | 0.0609 | 0.5447 | 0.0845
Linnet | 336.4 | 530 | 0.0615 | 0.5493 | 0.0855
Woodcock | 336.4 | 525 | 0.0619 | 0.5535 | 0.0866
Widgeon | 336.4 | 525 | 0.0617 | 0.5514 | 0.0861
Merlin | 336.4 | 520 | 0.0623 | 0.5574 | 0.0877
Trogon | 336.4 | 520 | 0.0623 | 0.5556 | 0.0871
Ostrich | 300 | 495 | 0.0689 | 0.5582 | 0.0869
Junco | 266.8 | 465 | 0.0767 | 0.5629 | 0.0872
Partridge | 266.8 | 460 | 0.0774 | 0.5673 | 0.0882
Spoonbill | 266.8 | 455 | 0.0781 | 0.5717 | 0.0892
Scaup | 266.8 | 455 | 0.0778 | 0.5696 | 0.0888
Waxwing | 266.8 | 450 | 0.0785 | 0.5756 | 0.0904
Penguin | 4/0 | 365 | 0.116 | 0.5877 | 0.1055
Pigeon | 3/0 | 315 | 0.143 | 0.6059 | 0.1093
Quail | 2/0 | 275 | 0.177 | 0.624 | 0.1133
Raven | 1/0 | 240 | 0.218 | 0.6421 | 0.1178
Robin | #1 | 210 | 0.271 | 0.6603 | 0.1226
Sparrow | #2 | 185 | 0.337 | 0.6785 | 0.1273
Sparate | #2 | 170 | 0.341 | 0.674 | 0.1289
Swan | #4 | 140 | 0.524 | 0.7148 | 0.1372
Swanate | #4 | 140 | 0.529 | 0.7105 | 0.141
Turkey | #6 | 105 | 0.819 | 0.7512 | 0.1465

## MV105 Cable Data
Size | Ampacity* | Resistance (ohms/kft) | Cap. Reactance (Mohms*kft) | Ind. Reactance (ohms/kft) | R1 (ohms/kft) | X1 (ohms/kft) | R0 (ohms/kft) | X0 (ohms/kft)
1000 | 525 | 0.023 | 0.034 | 0.039 | 0.024 | 0.039 | 0.29 | 0.149
750 | 455 | 0.03 | 0.038 | 0.041 | 0.031 | 0.041 | 0.31 | 0.166
500 | 370 | 0.045 | 0.043 | 0.044 | 0.046 | 0.044 | 0.343 | 0.194
350 | 305 | 0.064 | 0.048 | 0.046 | 0.064 | 0.046 | 0.374 | 0.214
250 | 250 | 0.089 | 0.054 | 0.048 | 0.09 | 0.048 | 0.409 | 0.233
4/0 | 230 | 0.105 | 0.056 | 0.05 | 0.106 | 0.049 | 0.43 | 0.245
3/0 | 200 | 0.132 | 0.061 | 0.051 | 0.133 | 0.051 | 0.462 | 0.257
2/0 | 175 | 0.167 | 0.065 | 0.053 | 0.168 | 0.053 | 0.502 | 0.269
1/0 | 155 | 0.211 | 0.069 | 0.055 | 0.212 | 0.055 | 0.55 | 0.28
* 90C in duct

## Xfmr Data
MVA | X/R | %Z
1 | 9 | 6%
2 | 10 | 6%
3 | 10 | 7%
4 | 10 | 7%
5 | 11 | 7%
6 | 11.5 | 7%
7 | 12 | 8%
8 | 13 | 8%
9 | 14 | 8%
10 | 15 | 8%
11 | 16 | 8%
12 | 17 | 8%
13 | 17.25 | 8%
14 | 17.5 | 8%
15 | 17.75 | 8%
16 | 18 | 8%
17 | 18.25 | 8%
18 | 18.5 | 8%
19 | 18.75 | 8%
20 | 19 | 8%
21 | 19.25 | 8%
22 | 19.75 | 8%
23 | 20.25 | 8%
24 | 20.75 | 8%
25 | 21.5 | 8%
26 | 21.75 | 10%
27 | 21.85 | 10%
28 | 21.9 | 10%
29 | 21.95 | 10%
30 | 22 | 10%
31 | 22.1 | 10%
32 | 22.3 | 10%
33 | 22.5 | 10%
34 | 22.65 | 10%
35 | 23 | 10%
36 | 23.15 | 10%
37 | 23.3 | 10%
38 | 23.65 | 10%
39 | 23.85 | 10%
40 | 24 | 10%
41 | 24.1 | 11%
42 | 24.2 | 11%
43 | 24.35 | 11%
44 | 24.45 | 11%
45 | 24.5 | 11%
46 | 24.6 | 11%
47 | 24.7 | 11%
48 | 24.8 | 11%
49 | 24.9 | 11%
50 | 25 | 11%
51 | 25.15 | 11%
52 | 25.3 | 11%
53 | 25.45 | 11%
54 | 25.6 | 11%
55 | 25.75 | 11%
56 | 25.9 | 11%
57 | 26.05 | 11%
58 | 26.2 | 11%
59 | 26.4 | 11%
60 | 26.5 | 11%
61 | 26.55 | 11%
62 | 26.7 | 11%
63 | 26.85 | 11%
64 | 27 | 12.5%
65 | 27.15 | 12.5%
66 | 27.3 | 12.5%
67 | 27.45 | 12.5%
68 | 27.6 | 12.5%
69 | 27.75 | 12.5%
70 | 28 | 12.5%
71 | 28.2 | 12.5%
72 | 28.4 | 12.5%
73 | 28.6 | 12.5%
74 | 28.8 | 12.5%
75 | 29 | 12.5%
76 | 29.2 | 12.5%
77 | 29.4 | 12.5%
78 | 29.6 | 12.5%
79 | 29.8 | 12.5%
80 | 30 | 12.5%
81 | 30.1 | 12.5%
82 | 30.2 | 12.5%
83 | 30.3 | 12.5%
84 | 30.4 | 12.5%
85 | 30.5 | 12.5%
86 | 30.6 | 12.5%
87 | 30.7 | 12.5%
88 | 30.8 | 12.5%
89 | 30.9 | 12.5%
90 | 31 | 12.5%
91 | 31.1 | 12.5%
92 | 31.2 | 12.5%
93 | 31.3 | 12.5%
94 | 31.4 | 12.5%
95 | 31.5 | 12.5%
96 | 31.6 | 12.5%
97 | 31.7 | 12.5%
98 | 31.8 | 12.5%
99 | 31.9 | 12.5%
100 | 32 | 12.5%
101 | 32.1 | 13%
102 | 32.2 | 13%
103 | 32.3 | 13%
104 | 32.4 | 13%
105 | 32.5 | 13%
106 | 32.6 | 13%
107 | 32.7 | 13%
108 | 32.8 | 13%
109 | 32.9 | 13%
110 | 33 | 13%

## Inverter Data
OEM | Model | Real Power 1.0PF 35C (kW) | Apparent Power (kVA) | Short Circuit (kA)
SMA | SC4000 | 3760 | 4000
SMA | SC4200 | 3948 | 4200 |  | SMA Data | https://docs.google.com/spreadsheets/d/1wShBEL0oUZ9qbZo1S_2OusbxvHG40z6pgJnJXQOugQk/edit#gid=0
SMA | SC4400 | 4136 | 4400
SMA | SC4600 | 4324 | 4600
SMA | SHP125 | 125 | 125
SMA | SHP150 | 150 | 150